## Pump Efficiency
g | 9.81
Cpw | 4.187
Suction Pressure (kPa) | 424
Discharge Pressure (kPa) | 8609
Suction Temperature (°C) | 29.6405
Discharge Temperature (°C) | 30.63
Delta Pressure (kPa) | 8185
Delta Temperature (°C) | 0.9895
Delta Pressure (meters) | 834.3527
Delta Temperature (mK) | 989.5
Efficiency | 66.3934
g = 9.81
t = milli Kelvin mK (Take °C add 273 and multiply by 1000 to get mK)
p = meters (but you can keep the formula in kPa and take out the g in the formula because you divide kPa by g to get meters but in the formula you multiply it with g again.
Cpw = 4.187
This formula effectively yields the following formula:
| STD | PK | OP
|  | 60 |  | 1
|  | 60 |  | 2
| 60 |  |  | 3
| 60 |  |  | 4
| 60 |  |  | 5
| 60 |  |  | 6
| 60 |  |  | 7
| 60 |  |  | 8
| 60 |  |  | 9
| 60 |  |  | 10
| 60 |  |  | 11
| 60 |  |  | 12
| 60 |  |  | 13
|  | 60 |  | 14
|  | 60 |  | 15
| 60 |  |  | 16
| 60 |  |  | 17
| 60 |  |  | 18
| 60 |  |  | 19
| 60 |  |  | 20
| 60 |  |  | 21
| 60 |  |  | 22
| 60 |  |  | 23
|  | 60 |  | 24

## Refrigeration
COP = Co-efficient Of Performance
Cpw | 4.187 |  | MWR = Mega Watt Refrigeration
Efficiency (ɳ) | 0.85 |  | ME = Machine Power (in Mega Watt - MW)
Cpw = 4.187
t1 (Water In Temperature) | 6.9 | °C
t2 (Water Out Temperature) | 2.7 | °C | Q = Water Flow (in liters per second - l/s)
∆t (t1 - t2) | 4.2 | °C | I1, I2 = Motor 1 Current, Motor 2 Current in Ampere (A)
Water Flow (Q) | 416 | l/s
V = Potential difference in Voltage
Voltage | 6600 | V | ɳ = motor efficiency
Current 1 | 98 | A
Current 2 | 53 | A
MWR(evaporator) | 7.3155 | MW
Machine Power (ME) | 1.4672 | MW
COP | 4.9859

## Time
Time Begin | 5:33
Time to work | 14:00
Time End | 19:26
Time Difference | 5:26